| LHC- - - 1999-09-22 |
| --- |
| MPS Commissioning Procedure |
| The commissioning of the LHC machine protection system MPS aspects of the Warm magnet INTERLOCK system commissioning |
| Abstract This document describes the set of tests which will be carried-out to validate for operation the machine protection aspects of the LHC Warm Magnet Interlock system. The area concerned by these tests extends over the whole LHC machine for each of the two LHC beams. These tests include the Hardware Commissioning, the machine check-out and the tests with beam. |
| Prepared by : Pierre Dahlen Iván Romera | Checked by : Reyes ALEMANY FERNANDEZ Gianluigi ARDUINI Ralph ASSMANN Roger BAILEY Andy BUTTERWORTH Etienne CARLIER Pierre DAHLEN Bernd DEHNING Brennan GODDARD Magali GRUWE Bernhard HOLZER Eva Barbara HOLZER Verena KAIN Mike LAMONT Alick MACPHERSON Laurette PONCE Bruno PUCCIO Stefano REDAELLI Mariusz SAPINSKI Ruediger SCHMIDT Jim STRAIT Benjamin TODD Jan UYTHOVEN Walter VENTURINI DELSOLARO Jorg WENNINGER Christos ZAMANTZAS Markus ZERLAUTH | Approved by: Rüdiger Schmidt Jorg Wenninger |
| History of Changes |
| Rev. No. | Date | Pages | Description of Changes |
| 0.1 0.2 0.3 0.4 0.5 0.6 | 2007-06-18 2007-09-07 2008-04-28 2009-01-12 2009-01-14 2009-02-25 | 12 11 11 11 | First draft for circulation. Comments added by J Uythoven and A Macpherson. Document updated for release Update document with experience from 2008 commissioning Minor corrections prior to release for approval Including comments after approval round Update References Add additional verification in Test 1 of chapter 7.2: Verify that the user permit towards the BIS is removed before the power permit of the converter is removed. |

Table of Contents

1.	Introduction	4

2.	Scope	4

3.	Purpose	4

4.	The WARM MAGNET INTERLOCK SyStem as a USER OF THE BEAM INTERLOCK SYSTEM	5

4.1	Redundant User Permit Signals	5

4.2	internal Redundancy for the User_Permit Signals	6

4.3	The Architecture of the Warm Magnet Interlock System	7

5.	Tests performed during the hardware commissioning	8

6.	Link to other equipment	8

7.	SYSTEM TESTS DURING THE MACHINE CHECKOUT	8

7.1	Entry Conditions required to perform tests	8

7.2	Description of the tests	9

7.3	Exit Conditions and Status after the system tests	10

8.	Tests with beam	10

9.	References	11

APPENDIX I - List of connections between WIC and BIS	11

# Introduction

After the qualification for operation of the individual systems of a sector, validation and specific studies of each equipment as a whole will be carried-out in the context of the machine protection system (MPS) commissioning.

This document describes the sequence of tests which validate the interface of the LHC warm Magnet Interlock System and the LHC Beam Interlock System for the 8 individual Warm Magnet Interlock Controllers installed in the LHC.

# Scope

This document covers the tests which will be carried-out to condition and validate for operation all the components of the Warm Magnet Interlock System with the machine protection system for LHC beam 1 and 2. The area concerned by these tests is the whole LHC ring. The equipments concerned are Power Converters and normal conducting magnets connected to the Warm Magnet Interlock Controller in the insertion regions to guarantee a beam dump request via hardwired links to the Beam Interlock System in case of powering failures.

# Purpose

This document

Gives a comprehensive list of the components which will be the object of the tests (WIC, BIS).

Describes in detail the procedures which will be applied for these tests and their sequence.

List exit conditions from the procedures

Each test has in front one of the following letters, defining at which interval or at which occasion the described test needs to be repeated (in the column labelled Repetition):

| N | Not to be repeated |
| --- | --- |
| S | To be repeated after every Shutdown |
| P | Periodical repetition required, like 1 x per month; details to be defined in text |
| O | To be repeated when LHC optics is changed |
| X | To be repeated when crossing scheme is changed |

This document is meant to be the reference document for the checklist which will be used during the commissioning of the MPS. Results of the tests will be documented in the MTF database.

# The WARM MAGNET INTERLOCK SyStem as a USER OF THE BEAM INTERLOCK SYSTEM

## Redundant User Permit Signals

All normal conducting magnets in the LHC are considered essential for continuous beam operation and any failure in the magnet powering should result in an immediate beam dump. Only after the beams are dumped, the shut down of the appropriate power converter is requested by the WIC as shown in Figure 1.

Figure 1: Signal exchange for a beam dump request from the warm magnet interlock controller towards the Beam Interlock System (BIS) and the LHC Beam Dumping System (LBDS).

According to the BIS requirements, two completely independent USER_PERMIT_A and USER_PERMIT_B signals are provided by the WIC as shown in Figure 2. A USER_PERMIT = FALSE on either of these lines will initiate a beam dump request of both beams at the same time.

Figure 2: Signal exchange between the WIC and the CIBUS of the Beam Interlock System (BIS)

## internal Redundancy for the User_Permit Signals

The safety of the link between the Warm Magnet Interlock System and the BIS is based on the redundancy of the USER_PERMIT signals.

As described in Figure 3, if a powering failure event occurs in any of the power converters managed by a warm magnet interlock controller, it will be noticed by two independent systems, a high-speed Boolean Processor (FM-352) and the PLC of the WIC.

In case an over temperature is detected in one of the normal conducting magnets, the PLC has the time to first request a beam dump and only afterwards shut down the power converter, thus avoiding the magnetic field decaying while the beams are still present.

As the response time of the PLC is not sufficiently fast for all failure scenarios, a high-speed Boolean Processor based solution has been chosen to realise the redundant signal path for the beam dump request. The response time is about 1 microsecond for the Boolean Processor, whilst it is in the order of some 100 milliseconds for the PLC. This fast reaction time is required due to the fact that in the case of a powering failure, the power converter will immediately shut down itself and the beam dump request has to be relayed quickly to the BIS (avoiding an additional PLC cycle).

- Boolean Processor: This device provides 12 digital inputs and 8 digital outputs, and triggers a beam dump request in case of a power converter failure.

- PLC: the PLC reads inputs coming from both, the magnets and power converters and will trigger a beam dump request in case an overheating is detected in a magnet or a power converter reports an internal failure.

Figure 3: Internal Redundancy for the User Permit Signals

## The Architecture of the Warm Magnet Interlock System

The Warm Magnet Interlock Controller is a user system of the Beam Interlock System, requesting a beam dump of the two beams in case of failures in the magnet powering of normal conducting circuits.

A total of 8 BIS User Interfaces (CIBUS) for the WIC are installed in the LHC to manage the beam dump requests sent by the WICs (see Figure 4 as a configuration example). The signals are exchanged via hardwired links between the WIC and the BIS User Interface, using current loops for a fail safe transmission of the signal. A list of the BIS User interfaces to be connected to the WIC is given at the end the document (APPENDIX I - List of connections between WIC and BIS).

# Tests performed during the hardware commissioning

The Warm Magnet Interlock System has already been fully commissioned together with the power converters and normal conducting magnets during the corresponding hardware commissioning phase [2]. The commissioning of the interfaces between the Warm Magnet Interlock Controller and the Beam Interlock Controller is described in section 7. As indicated previously, every WIC and Power Converter in an insertion region needs to be installed, commissioned and fully operational before these final tests can be performed.

# Link to other equipment

Each interlock controller receives information from the following systems:

PC: The power converters are connected to WIC via hardwired links. Any failure provoked by a power converter is detected by the WIC which will trigger a beam dump request.

Magnets: Connected to the WIC via hardwired links. Any over temperature detected by one of the thermo switches on the magnets is read by the WIC, which will trigger a beam dump request.

The WICs require no other inputs and only sends outputs to the BIS. As such, no additional tests are required in this section. In particular, no additional action is foreseen by the WIC when it receives a BEAM_INFO = FALSE.

# SYSTEM TESTS DURING THE MACHINE CHECKOUT

The integral system should be tested from the CERN Control Centre (CCC), simulating as much as possible future operation with beam. These tests are ideally performed automatically in order to minimize the test times required and to facilitate further maintenance.

Tests to be carried out are: Beam dump triggered by PC event; Beam dump triggered by over-temperature in a magnet and operator request (removal of power permit).

## Entry Conditions required to perform tests

Successful completion of the individual system tests and hardware commissioning phases of all Warm Magnet Interlock Controllers of the concerned insertion region.

Nominal operating conditions for all electrical circuits connected to the warm magnet interlock controllers subject to the test. The tests can be performed at zero current; only the control part of the power converters needs to be fully operational.

The Logging System must be available

BIS operational in the insertion region

Mains network and UPS supplies operational in the insertion region

## Description of the tests

Once all faults are cleared and all power converters in the insertion region are switched on, any of the following conditions will provoke a beam dump request in an interlock controller:

- Failure of magnet powering (Internal converter failure)

- Over temperature in a magnet (Magnet temperature above the limit of 65ºC)

- Operator request via the Supervision Application

The following three steps have to be performed to successfully commission the interface of the WIC with the Beam Interlock System:

| Test |  | Action | Group(s) Responsible |
| --- | --- | --- | --- |
| 1 | S | Test beam dump triggered by over-temperature in a magnet. Circuit by circuit (for every magnet) connected to the WIC: Verify that all PC_PERMIT signals are OK Verify USER_PERMIT TO BIS is OK Enable signal to simulate an over temperature in the magnet (CMD_MAG_OVERTEMP_TEST) Check that ST_MAG_OVERTEMP and PC_PERMIT signals for this magnet are removed for a few seconds Check that USER_PERMIT TO BIS has been removed BEFORE the power permit of the power converter is removed Validate the according trigger of the WIC event in the BIS history buffer and determine the time delays (for both the A and B beam permit channels). Validate that the output of the FM352 stays TRUE during the test | TE/MPE |

| Test |  | Action | Group(s) Responsible |
| --- | --- | --- | --- |
| 2 | S | Test beam dump triggered by PC event: For every Power Converter connected to the WIC: Verify that: All PC_PERMIT signals are OK All ST_FAILURE_WIC signals are OK USER_PERMIT TO BIS is OK Send CMD_FABORT_WIC to the PC Check that: PC_PERMIT has been removed ST_FAILURE_WIC is NOT OK USER_PERMIT TO BIS has been removed Validate the according trigger of the WIC event in the BIS history buffer and determine the time delays (for both the A and B beam permit channels). Validate that the output of the FM352 changes to FALSE when the powering failure is triggered. Validate that the time response of the FM352 is as expected in the order of a few us. | TE/MPE TE/EPC |
| 3 | S | Confirm that an operator can set the WIC USER_PERMIT to FALSE. Verify that: All PC_PERMIT signals are OK All ST_FAILURE_WIC signals are OK USER_PERMIT TO BIS is removed upon the operator request | TE/MPE |

## Exit Conditions and Status after the system tests

After these tests, the machine protection aspects of the Warm Magnet Interlock System have been validated for all the systems that may trigger a Beam Dump request connected through the WIC.

# Tests with beam

To validate the interfaces between the Warm Magnet Interlock System and the BIS there is in principle no need to perform any tests with beam. However, to study the time delays (e.g. after a powering failure until the completion of the beam dump) a number of studies could be performed with low beam intensity to evaluate the overall performance of the Machine Protection Systems.

Beam tests of the WIC will be performed at the same time as for the FMCMs, see Ref. [3], since those tests will automatically also trigger WIC interlocks.

# References

[1] B. Todd and B.Puccio; ‘MPS Aspects of the Beam Interlock System: Commissioning’; EDMS Doc: LHC-OP-MPS-0004

[2] P.Dahlen, B. Bellesia et al.; ‘General Procedure for the Commissioning of the Warm Electrical Circuits’; EDMS Doc: LHC-MW-HCP-0002

[3] M. Zerlauth et al.; ‘MPS Aspects of the Fast Magnet Current Change Monitor Commissioning’; EDMS Doc: LHC-OP-MPS-008

# APPENDIX I - List of connections between WIC and BIS

| Point | WIC Name | CIBUS Location | BIC Name |
| --- | --- | --- | --- |
| 1 | CIW.US15.LR1 | MYWIC01=US15W2 | CIB.US15.L1 |
| 2 | CIW.UA23.LR2 | MYWIC01=UA23 | CIB.UA23.L2 |
| 3 | CIW.UJ33.LR3 | MYWIC01=UJ33 | CIB.UJ33.U3 |
| 4 | CIW.UA47.LR4 | MYWIC01=UA47 | CIB.UA47.R4 |
| 5 | CIW.USC55.LR5 | MYWIC01=USC55 | CIB.USC55.L5 |
| 6 | CIW.US65.LR6 | MYWIC01=US65 | CIB.UA63.L6 |
| 7 | CIW.TZ76.LR7 | MYWIC01=TZ76 | CIB.TZ76.U7 |
| 8 | CIW.US85.LR8 | MYWIC01=US85 | CIB.UA83.L8 |

# Text boxes

WIC

BIS

User_Permit

LBDS

Beam_Permit

Beam_Info

Figure 4: Principle of the Warm Magnets Interlock System for point 8 in the LHC with FM 352